## Slide 1: Phase 1 equals 7% of PJM's capacity shortfall and the full campus 29%, so Ironwood should connect in phases
Megawatts, PJM 2028/29 capacity auction
PJM shortfall, 2028/29
6,831 MW
Full Ironwood campus
2,000 MW
Phase 1
480 MW
Phase 1 alone adds about $57M a year in capacity charges at today's auction price
Data centers drove $29.4B, or 46%, of PJM capacity charges over the last four auctions
KGE can serve 480 MW after upgrades but cannot yet time or price 2,000 MW
Each later phase waits for new PJM supply and a clean step on track
Source: PJM 2028/29 Base Residual Auction report; PJM Independent Market Monitor, 27 July 2026; case packet; SLAM analysis (leepr)
Notes: Start with scale. Phase 1 is 480 MW, about 7% of the capacity PJM could not find in its last auction. The full campus would be 29% of that gap, and households already pay for it, since data centers drove 46% of capacity charges in the last four auctions. So we commit to phase 1 now and build later phases only when PJM adds supply and the clean step is on track.

## Slide 2: The hybrid is the only option that meets the 2035 clean step and rides through PJM emergencies, for $20 more per MWh
Phase 1 energy cost, $ per MWh, 480 MW
$93.6
Grid only
$67.1
Onsite gas
$103.3
Clean contracts only
$103.9
Grid + battery only
$113.6
Hybrid: battery + clean contracts
Costs about $84M a year more than grid only, paid by the customer under its 20-year contract
Cuts CO2 by 32%, about 365,000 t a year
Meets the 32% clean firm step the state sets for 2035
Battery income from PJM's energy and reserve markets is upside we did not count
Source: EIA; PJM 2028/29 auction and 2025 State of the Market; LevelTen PPA index; NREL 2025 battery costs; EPA eGRID2023; PA GRID Standards; SLAM analysis (leepr)
Notes: These are the supply options the case lists, priced per MWh for phase 1. Grid only is $93.60. The hybrid adds clean energy contracts for the state's 32% clean step and a 4-hour battery for grid emergencies, which brings it to $113.60. The customer asked for reliable power and progress on its carbon goals, so the $84M a year premium sits in its 20-year power contract rather than on households.

## Slide 3: Onsite gas looks cheapest, yet it emits 62% more CO2 than the grid and loses its edge if gas prices climb
Phase 1 energy cost, $ per MWh
$67.1
Gas at forecast price
$111.7
Gas at 2024 PA industrial price
$93.6
Grid only
$113.6
Hybrid
CO2, million t a year
1.85
Onsite gas
1.14
Grid only
0.77
Hybrid
Residents near the site asked for enforceable limits on generator emissions, and gas engines would run every hour of every day.
Source: EIA capital cost report (AEO2020) and Short-Term Energy Outlook; EIA Pennsylvania industrial gas price, 2024; EPA eGRID2023 RFC East; case packet; SLAM analysis (leepr)
Notes: Gas is the obvious objection, so we answer it directly. At the forecast gas price, onsite engines cost $67 per MWh. At the price Pennsylvania industrial users actually paid in 2024, the same plant costs $112, about what the hybrid costs. Gas also emits 62% more CO2 than the grid, fails the 2035 clean step, and puts engines next to the homes that asked for emission limits.

## Slide 4: A 4-hour battery keeps Ironwood's critical servers running through every PJM emergency its zone saw last summer
Normal hours
PJM grid
480 MW
All servers, 480 MW
Idle
Battery, 1,920 MWh
Emergency, first 4 hours
PJM grid
0 MW
All servers, 480 MW
480 MW
Battery, 1,920 MWh
Emergency, hours 5 to 8
PJM grid
0 MW
Critical servers, 240 MW
240 MW
Battery, 1,920 MWh
PJM's 2025 emergencies in the Met-Ed zone lasted 3.2 to 7 hours
The battery carries the whole campus for 4 hours, or the critical half for 8
Only flexible AI training pauses after hour 4, a limit we write into the contract
PJM gets 480 MW back in the hours it is short
Source: PJM demand response event report, December 2025; Duke University Nicholas Institute, Rethinking Load Growth (2025); case packet; SLAM analysis (leepr)
Notes: This settles the case's hardest conflict. PJM wants the campus to cut load in an emergency, and the customer says continuous operation is essential. The battery lets Ironwood drop its grid draw to zero while it keeps running. Last summer PJM's emergencies in this zone lasted 3 to 7 hours. The battery covers the whole campus for 4 hours, or the critical half for 8, so only flexible training jobs ever pause, and that limit goes in the contract.

## Slide 5: Ironwood pays for every grid upgrade it causes, so Met-Ed households and the 600-person plant do not
Cost or risk | Who pays | How it is enforced
Substation and lines built only for Ironwood | Slate Ridge, up front | Paid before construction, under the PUC's "but for" rule
Risk the load never arrives | Slate Ridge | A minimum bill of 80% of contracted demand, backed by collateral
Leaving early or shrinking | Slate Ridge | An exit fee covering unrecovered costs or remaining minimum charges
Clean energy for the 2035 step | The anchor customer | Contracts for 32% clean firm power, 1,346 GWh a year by 2035
Strain on PJM in emergencies | Ironwood | The battery takes 480 MW off the grid in those hours
The PUC's model tariff is guidance that utilities may adopt. KGE would sign its terms with Met-Ed anyway, in writing.
Source: PA PUC Large Load Model Tariff final order, 13 May 2026 (M-2025-3054271); PA GRID Standards; Met-Ed tariff service territory; case packet; SLAM analysis (leepr)
Notes: The case asks who pays if demand projections change. Pennsylvania's model tariff answers most of it: a large load pays for upgrades built because of it, keeps paying 80% of its contracted demand even if it uses less, posts collateral, and pays an exit fee if it leaves. The tariff is only guidance, so utilities do not have to use it. We would have KGE sign those terms with Met-Ed anyway, which keeps the cost off households and the 600-person manufacturer.

## Slide 6: Across every input range we tested, the hybrid costs between $11 and $25 more per MWh than grid power
Hybrid premium over grid only, $ per MWh, when one input moves to its low or high end
Base case $20.02
Wholesale power price
$33.74 to $74.06 per MWh
$12.55
$25.46
Battery cost
$207 to $365 per kWh
$10.94
$22.23
Solar PPA price
$52.65 to $83.79 per MWh
$10.94
$20.90
PJM capacity price
$270 to $333 per MW-day
$19.67
$22.31
Retail grid price
$85.10 to $110.40 per MWh
Moves both options equally
Source: SLAM analysis (leepr); input ranges from PJM, LevelTen, NREL and EIA
Notes: Use this if a judge asks how sure we are. Grid price moves grid power and the hybrid by the same amount, so the gap between them does not change. The premium only moves with the wholesale price, the battery cost, the clean contract price and the capacity price, and it stays between about $11 and $25 per MWh.

## Slide 7: Every power input comes from a public source and carries a tested range
Input | Value used | Range tested | Source
Retail grid price | $93.60 per MWh | $85.10 to $110.40 | EIA, Pennsylvania industrial retail sales
PJM capacity price | $325 per MW-day | $270 to $333 | PJM 2028/29 Base Residual Auction
Wholesale energy price | $50.73 per MWh | $33.74 to $74.06 | PJM 2025 State of the Market
Clean contract (solar PPA) price | $81.03 per MWh | $52.65 to $83.79 | LevelTen PPA index, Q4 2025
Clean firm share by 2035 | 32% | 10% in 2027, 14.5% in 2030 | PA GRID Standards
Grid CO2 intensity | 597 lb per MWh | Up to 1,176 for marginal plants | EPA eGRID2023, RFC East
Battery cost | $334 per kWh | $207 to $365 | NREL 2025 battery cost update
Battery duration | 4 hours | Met-Ed and PPL zone events ran 3.2 to 7 hours in 2025 | PJM demand response event report, Dec 2025
Gas price | $3.48 per MMBtu | $3.16 to $8.86 | EIA Short-Term Energy Outlook; EIA PA industrial, 2024
Gas engine plant cost | $1,810 per kW | $1,700 to $2,400 | EIA capital cost report (AEO2020)
Source: leepr data file data/cases/ironwood-energy.json, each input with its link and date checked
Notes: Every number in the power section traces to this table. The model and its sources are in the leepr repository, so any figure can be checked live.